## Energy audit- correct version
Game Level | Task # | Floor | Room ID | Room | Equipment | Hotspot ID | Revised HotSpot ID Naming convention | Source (in game) | Power (W) | No of hours | Standby power | Standby hours | Quanitity | Diversity Factor | Energy per day | No of days | Annual energy | Equipment | Light | AC | Totals
L1 | T09 | GF | Z01 | Male toilet | Hanging Lights | GF_Z01_H01 | L1_T09_GF_Z01_H001 | On click | 21.5 | 8 |  |  | 1 | 0.7 | 120.4 | 260 | 31304 | 1735 | 762.4
L1 | T09 | GF |  |  | Tube lights | GF_Z01_H02 | L1_T09_GF_Z01_H002 | On click | 21.5 | 8 |  |  | 5 | 0.7 | 602 | 260 | 156520
L1 | T09 | GF |  |  | mirror light | GF_Z01_H03 | L1_T09_GF_Z01_H003 | On click | 5 | 8 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | GF |  |  | hand dryer | GF_Z01_H04 | L1_T09_GF_Z01_H004 | Nameplate | 1500 | 0.7 | 1 | 13 | 1 | 1 | 1063 | 260 | 276380
L1 | T09 | GF |  |  | Exhaust fan | GF_Z01_H05 | L1_T09_GF_Z01_H005 | On click | 20 | 12 |  |  | 4 | 0.7 | 672 | 260 | 174720
L1 | T09 | GF | Z02 | Meeting room 1 | Light | GF_Z02_H01 | L1_T09_GF_Z02_H006 | On click | 21.5 | 3 |  |  | 1 | 0.7 | 45.15 | 260 | 11739 | 976 | 45.15
L1 | T09 | GF |  |  | TV | GF_Z02_H02 |  | On click | 448 | 2 |  |  | 1 | 1 | 896 | 260 | 232960
L1 | T09 | GF |  |  | Laptop charging | GF_Z02_H03 |  | Clampmeter | 40 | 1 |  |  | 8 | 0.25 | 80 | 260 | 20800
L1 | T09 | GF | Z03 | Meeting room 2 | Light | GF_Z03_H01 |  | On click | 21.5 | 3 |  |  | 1 | 0.7 | 45.15 | 260 | 11739 | 976 | 45.15
L1 | T09 | GF |  |  | TV | GF_Z03_H02 |  | On click | 448 | 2 |  |  | 1 | 1 | 896 | 260 | 232960
L1 | T09 | GF |  |  | Laptop charging | GF_Z03_H03 |  | Clampmeter | 40 | 1 |  |  | 8 | 0.25 | 80 | 260 | 20800
L1 | T09 | GF | Z04 | Classroom 1 | Light | GF_Z04_H01 |  | On click | 21.5 | 3 |  |  | 4 | 0.7 | 180.6 | 260 | 46956 | 1048 | 180.6
L1 | T09 | GF |  |  | TV | GF_Z04_H02 |  | On click | 448 | 1 |  |  | 1 | 1 | 448 | 260 | 116480
L1 | T09 | GF |  |  | Laptop charging | GF_Z04_H03 |  | Clampmeter | 40 | 1 |  |  | 30 | 0.5 | 600 | 260 | 156000
L1 | T09 | GF | Z05 | Classroom 2 | Light | GF_Z05_H01 |  | On click | 21.5 | 3 |  |  | 4 | 0.7 | 180.6 | 260 | 46956 | 913.6 | 180.6
L1 | T09 | GF |  |  | TV | GF_Z05_H02 |  | On click | 448 | 0.7 |  |  | 1 | 1 | 313.6 | 260 | 81536
L1 | T09 | GF |  |  | Laptop charging | GF_Z05_H03 |  | Clampmeter | 40 | 1 |  |  | 30 | 0.5 | 600 | 260 | 156000
L1 | T09 | GF | Z06 | AHU | AHU rated power | GF_Z06_H01 |  | Nameplate | 1500 | 16 | 50 | 8 | 1 | 1 | 24400 | 260 | 6344000 | 0 | 632.1 | 24400
L1 | T09 | GF |  |  | Tube lights | GF_Z06_H02 |  | On click | 21.5 | 2 |  |  | 3 | 0.7 | 90.3 | 260 | 23478
L1 | T09 | GF | Z07 | Corridor | Hanging lights | GF_Z07_H01 |  | On click | 21.5 | 18 |  |  | 2 | 0.7 | 541.8 | 260 | 140868
L1 | T09 | GF | Z08 | Classroom 3 | Light | GF_Z08_H01 |  | On click | 21.5 | 2 |  |  | 5 | 0.7 | 150.5 | 260 | 39130 | 1408 | 150.5
L1 | T09 | GF |  |  | TV | GF_Z08_H02 |  | On click | 448 | 1 |  |  | 1 | 1 | 448 | 260 | 116480
L1 | T09 | GF |  |  | Laptop charging | GF_Z08_H03 |  | Clampmeter | 40 | 1 |  |  | 48 | 0.5 | 960 | 260 | 249600
L1 | T09 | GF | Z09 | Corridor | Hanging lights | GF_Z09_H01 |  | On click | 21.5 | 18 |  |  | 6 | 0.33333 | 774 | 260 | 201240 | 19.6 | 774
L1 | T09 | GF | Z10 | Reception area | Hanging lights | GF_Z10_H01 |  | On click | 21.5 | 18 |  |  | 2 | 0.7 | 541.8 | 260 | 140868 |  | 541.8
L1 | T09 | GF |  |  | Phone charging | GF_Z10_H02 |  | Clampmeter | 10 | 0.7 |  |  | 4 | 0.7 | 19.6 | 260 | 5096
L1 | T09 | GF |  | Elevator |  | GF_Z10_H03 |  | On click | 40 | 4 |  |  | 2
L1 | T09 | GF | Z11 | Storage room | Hanging lights | GF_Z11_H01 |  | On click | 21.5 | 2 |  |  | 2 | 0.5 | 43 | 260 | 11180 |  | 133.3
L1 | T09 | GF |  |  | Tube Lights | GF_Z11_H02 |  | On click | 21.5 | 1 |  |  | 6 | 0.7 | 90.3 | 260 | 23478
L1 | T09 | GF | Z12 | Corridor | Hanging lights | GF_Z12_H01 |  | On click | 21.5 | 18 |  |  | 2 | 1 | 774 | 260 | 201240 |  | 774
L1 | T09 | GF | Z13 | Meeting room 3 | Light | GF_Z13_H01 |  | On click | 21.5 | 3 |  |  | 1 | 0.7 | 45.15 | 260 | 11739 | 393.6 | 45.15
L1 | T09 | GF |  |  | TV | GF_Z13_H02 |  | On click | 448 | 0.7 |  |  | 1 | 1 | 313.6 | 260 | 81536
L1 | T09 | GF |  |  | Laptop charging | GF_Z13_H03 |  | Clampmeter | 40 | 1 |  |  | 6 | 0.33333 | 80 | 260 | 20800
L1 | T09 | GF | Z14 | Female toilet | Hanging Lights | GF_Z14_H01 |  | On click | 21.5 | 8 |  |  | 1 | 0.7 | 120.4 | 260 | 31304 | 2172 | 882.8
L1 | T09 | GF |  |  | Tube lights | GF_Z14_H02 |  | On click | 21.5 | 8 |  |  | 6 | 0.7 | 722.4 | 260 | 187824
L1 | T09 | GF |  |  | mirror light | GF_Z14_H03 |  | On click | 5 | 8 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | GF |  |  | hand dryer | GF_Z14_H04 |  | Nameplate | 1500 | 1 |  |  | 1 | 1 | 1500 | 260 | 390000
L1 | T09 | GF |  |  | Exhaust fan | GF_Z14_H05 |  | On click | 20 | 12 |  |  | 4 | 0.7 | 672 | 260 | 174720
L1 | T09 | GF | Z15 | Corridor | Hanging lights | GF_Z15_H01 |  | On click | 21.5 | 18 |  |  | 3 | 0.7 | 812.7 | 260 | 211302 |  | 812.7
L1 | T09 | GF | Z16 | Server room | Computers with monitor | GF_Z16_H01 |  | Clampmeter | 90 | 8 | 8 | 16 | 4 | 0.7 | 2374.4 | 260 | 617344 | 27858 | 903
L1 | T09 | GF |  |  | Printer | GF_Z16_H02 |  | Clampmeter | 180 | 3 | 30 | 21 | 1 | 1 | 1170 | 260 | 304200
L1 | T09 | GF |  |  | TV | GF_Z16_H03 |  | On click | 448 | 0.7 |  |  | 2 | 0.5 | 313.6 | 260 | 81536
L1 | T09 | GF |  |  | Server Rack | GF_Z16_H04 |  | On click | 500 | 24 |  |  | 4 | 0.5 | 24000 | 260 | 6240000
L1 | T09 | GF |  |  | Split AC (2TR) | GF_Z16_H05 |  | On click | 4923.1 | 12 | 5 | 12 | 1 | 1 | 59137.2 | 260 | 15375672 |  |  | 59137.2
L1 | T09 | GF |  |  | Hanging lights | GF_Z16_H06 |  | On click | 21.5 | 12 |  |  | 2 | 0.7 | 361.2 | 260 | 93912
L1 | T09 | GF |  |  | Tube Lights | GF_Z16_H07 |  | On click | 21.5 | 12 |  |  | 3 | 0.7 | 541.8 | 260 | 140868
L1 | T09 | GF | Z17 | Pantry | Fridge | GF_Z17_H01 |  | Nameboard | 1500 | 24 |  |  | 1 | 1 | 36000 | 260 | 9360000 | 41744 | 632.1
L1 | T09 | GF |  |  | Coffee maker | GF_Z17_H02 |  | On click | 250 | 2 | 5 | 22 | 2 | 0.5 | 610 | 260 | 158600
L1 | T09 | GF |  |  | Kettle | GF_Z17_H03 |  | On click | 1500 | 1 | 1 | 23 | 2 | 0.5 | 1523 | 260 | 395980
L1 | T09 | GF |  |  | Water purifier | GF_Z17_H04 |  | Nameboard | 100 | 3 | 10 | 21 | 6 | 0.5 | 1530 | 260 | 397800
L1 | T09 | GF |  |  | Wall Fans | GF_Z17_H05 |  | On click | 35 | 6 |  |  | 2 | 1 | 420 | 260 | 109200
L1 | T09 | GF |  |  | Microwave oven | GF_Z17_H06 |  | On click | 1500 | 1 | 7 | 23 | 1 | 1 | 1661 | 260 | 431860
[5 empty] | Vending machine | [7 empty] | 1
L1 | T09 | GF |  |  | Hanging lights | GF_Z17_H07 |  | On click | 21.5 | 6 |  |  | 2 | 0.7 | 180.6 | 260 | 46956
L1 | T09 | GF |  |  | Tube Lights | GF_Z17_H08 |  | On click | 21.5 | 6 |  |  | 5 | 0.7 | 451.5 | 260 | 117390
L1 | T09 | GF | Z18 | Gym | Treadmill | GF_Z18_H01 |  | On click | 500 | 1 | 5 | 23 | 3 | 0.33333 | 615 | 260 | 159900 | 702.6 | 105
L1 | T09 | GF |  |  | Bike | GF_Z18_H02 |  | On click | 55 | 0.3 | 3 | 23.7 | 2 | 0.5 | 87.6 | 260 | 22776
L1 | T09 | GF |  |  | Elliptical | GF_Z18_H03 |  | On click | 10 | 0.7 |  |  | 3 | 0.7 | 14.7 | 260 | 3822
L1 | T09 | GF |  |  | Hanging Lights | GF_Z18_H04 |  | On click | 21.5 | 1 |  |  | 6 | 0.7 | 90.3 | 260 | 23478
L1 | T09 | First floor | [13 empty] | 260 | 0
L1 | T09 | FF | Z01 | Male toilet | Hanging Lights | FF_Z01_H01 |  | On click | 21.5 | 8 |  |  | 1 | 0.7 | 120.4 | 260 | 31304 | 2172 | 882.8
L1 | T09 | FF |  |  | Tube lights | FF_Z01_H02 |  | On click | 21.5 | 8 |  |  | 6 | 0.7 | 722.4 | 260 | 187824
L1 | T09 | FF |  |  | mirror light | FF_Z01_H03 |  | On click | 5 | 8 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | FF |  |  | hand dryer | FF_Z01_H04 |  | Nameplate | 1500 | 1 |  |  | 1 | 1 | 1500 | 260 | 390000
L1 | T09 | FF |  |  | Exhaust fan | FF_Z01_H05 |  | On click | 20 | 12 |  |  | 4 | 0.7 | 672 | 260 | 174720
L1 | T09 | FF | Z02 | Open-plan office | Recessed ceiling panel lights | FF_Z02_H01 |  | On click | 21.5 | 16 |  |  | 16 | 0.7 | 3852.8 | 260 | 1001728 | 1820 | 3852.8
L1 | T09 | FF | Z02 |  | Laptop charging | FF_Z02_H02 |  | Clampmeter | 40 | 2 |  |  | 32 | 0.5 | 1280 | 260 | 332800
L1 | T09 | FF | Z03 |  | Printer | FF_Z03_H01 |  | Clampmeter | 180 | 3 | 30 | 21 | 1 | 1 | 540 | 260 | 140400
L1 | T09 | FF | Z04 | Open-plan office | Recessed ceiling panel lights | FF_Z04_H01 |  | On click | 21.5 | 16 |  |  | 20 | 0.7 | 4816 | 260 | 1252160 | 1340 | 4816
L1 | T09 | FF | Z04 |  | Laptop charging | FF_Z04_H02 |  | Clampmeter | 40 | 1 |  |  | 40 | 0.5 | 800 | 260 | 208000
L1 | T09 | FF | Z05 |  | Printer | FF_Z05_H01 |  | Clampmeter | 180 | 3 | 30 | 21 | 1 | 1 | 540 | 260 | 140400
L1 | T09 | FF | Z06 | AHU | AHU rated power | FF_Z06_H01 |  | Nameplate | 1500 | 12 | 50 | 12 | 1 | 1 | 18600 | 260 | 4836000 | 0 | 45.15 | 18600
L1 | T09 | FF |  |  | Tube lights | FF_Z06_H02 |  | On click | 21.5 | 1 |  |  | 3 | 0.7 | 45.15 | 260 | 11739
L1 | T09 | FF | Z07 | Corridor | Hanging lights | FF_Z07_H01 |  | On click | 21.5 | 18 |  |  | 1 | 0.7 | 270.9 | 260 | 70434 |  | 270.9
L1 | T09 | FF | Z08 | Cabin | Recessed ceiling panel lights | FF_Z08_H01 |  | On click | 21.5 | 12 |  |  | 1 | 1 | 258 | 260 | 67080 | 47 | 258
L1 | T09 | FF |  |  | Laptop charging | FF_Z08_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | FF |  |  | Phone charging | FF_Z08_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | FF | Z09 | Cabin | Recessed ceiling panel lights | FF_Z09_H01 |  | On click | 21.5 | 12 |  |  | 1 | 1 | 258 | 260 | 67080 | 47 | 258
L1 | T09 | FF |  |  | Laptop charging | FF_Z09_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | FF |  |  | Phone charging | FF_Z09_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | FF | Z10 | Cabin | Recessed ceiling panel lights | FF_Z10_H01 |  | On click | 21.5 | 12 |  |  | 1 | 1 | 258 | 260 | 67080 | 47 | 258
L1 | T09 | FF |  |  | Laptop charging | FF_Z10_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | FF |  |  | Phone charging | FF_Z10_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | FF | Z11 | Elevator | Hanging lights | FF_Z11_H01 |  | On click | 21.5 | 2 |  |  | 1 | 1 | 43 | 260 | 11180 |  | 43
L1 | T09 |  |  |  | Elevator |  |  | On click | 9000 | 2 | 300 | 22 | 2 | 0.7 | 27240 | 260 | 7082400 | 27240
L1 | T09 | FF | Z12 | Cabin | Recessed ceiling panel lights | FF_Z12_H01 |  | On click | 21.5 | 12 |  |  | 1 | 1 | 258 | 260 | 67080 | 47 | 258
L1 | T09 | FF |  |  | Laptop charging | FF_Z12_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | FF |  |  | Phone charging | FF_Z12_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | FF | Z13 | Cabin | Recessed ceiling panel lights | FF_Z13_H01 |  | On click | 21.5 | 12 |  |  | 1 | 1 | 258 | 260 | 67080 | 47 | 258
L1 | T09 | FF |  |  | Laptop charging | FF_Z13_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | FF |  |  | Phone charging | FF_Z13_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | FF | Z14 | Cabin | Recessed ceiling panel lights | FF_Z14_H01 |  | On click | 21.5 | 12 |  |  | 1 | 1 | 258 | 260 | 67080 | 47 | 258
L1 | T09 | FF |  |  | Laptop charging | FF_Z14_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | FF |  |  | Phone charging | FF_Z14_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | FF | Z15 | Corridor | Hanging lights | FF_Z15_H01 |  | On click | 21.5 | 18 |  |  | 1 | 0.7 | 270.9 | 260 | 70434 |  | 270.9
L1 | T09 | FF | Z16 | Meeting room 3 | Light | FF_Z16_H01 |  | On click | 21.5 | 4 |  |  | 1 | 0.7 | 60.2 | 260 | 15652 | 616 | 60.2
L1 | T09 | FF |  |  | TV | FF_Z16_H02 |  | On click | 448 | 1 |  |  | 1 | 1 | 448 | 260 | 116480
L1 | T09 | FF |  |  | Laptop charging | FF_Z16_H03 |  | Clampmeter | 40 | 1 |  |  | 6 | 0.7 | 168 | 260 | 43680
L1 | T09 | FF | Z17 | Cabin | Recessed ceiling panel lights | FF_Z17_H01 |  | On click | 21.5 | 12 |  |  | 1 | 1 | 258 | 260 | 67080 | 47 | 258
L1 | T09 | FF |  |  | Laptop charging | FF_Z17_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | FF |  |  | Phone charging | FF_Z17_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | FF | Z18 | Cabin | Recessed ceiling panel lights | FF_Z18_H01 |  | On click | 21.5 | 12 |  |  | 1 | 1 | 258 | 260 | 67080 | 47 | 258
L1 | T09 | FF |  |  | Laptop charging | FF_Z18_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | FF |  |  | Phone charging | FF_Z18_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | FF | Z19 | Cabin | Recessed ceiling panel lights | FF_Z19_H01 |  | On click | 21.5 | 12 |  |  | 1 | 1 | 258 | 260 | 67080 | 47 | 258
L1 | T09 | FF |  |  | Laptop charging | FF_Z19_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | FF |  |  | Phone charging | FF_Z19_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | FF | Z20 | Cabin | Recessed ceiling panel lights | FF_Z20_H01 |  | On click | 21.5 | 12 |  |  | 1 | 1 | 258 | 260 | 67080 | 47 | 258
L1 | T09 | FF |  |  | Laptop charging | FF_Z20_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | FF |  |  | Phone charging | FF_Z20_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | FF | Z21 | Cabin | Recessed ceiling panel lights | FF_Z21_H01 |  | On click | 21.5 | 12 |  |  | 1 | 1 | 258 | 260 | 67080 | 47 | 258
L1 | T09 | FF |  |  | Laptop charging | FF_Z21_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | FF |  |  | Phone charging | FF_Z21_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | FF | Z22 | Cabin | Recessed ceiling panel lights | FF_Z22_H01 |  | On click | 21.5 | 12 |  |  | 1 | 1 | 258 | 260 | 67080 | 47 | 258
L1 | T09 | FF |  |  | Laptop charging | FF_Z22_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | FF |  |  | Phone charging | FF_Z22_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | FF | Z23 | Open-plan office | Recessed ceiling panel lights | FF_Z23_H01 |  | On click | 21.5 | 16 |  |  | 20 | 1 | 6880 | 260 | 1788800 | 1340 | 6880
L1 | T09 | FF | Z23 |  | Laptop charging | FF_Z23_H02 |  | Clampmeter | 40 | 1 |  |  | 40 | 0.5 | 800 | 260 | 208000
L1 | T09 | FF | Z24 |  | Printer | FF_Z24_H01 |  | Clampmeter | 180 | 3 | 30 | 21 | 1 | 1 | 540 | 260 | 140400
L1 | T09 | FF | Z25 | Open-plan office | Recessed ceiling panel lights | FF_Z25_H01 |  | On click | 21.5 | 16 |  |  | 16 | 1 | 5504 | 260 | 1431040 | 1180 | 5504
L1 | T09 | FF | Z25 |  | Laptop charging | FF_Z25_H02 |  | Clampmeter | 40 | 1 |  |  | 32 | 0.5 | 640 | 260 | 166400
L1 | T09 | FF | Z26 |  | Printer | FF_Z26_H01 |  | Clampmeter | 180 | 3 | 30 | 21 | 1 | 1 | 540 | 260 | 140400
L1 | T09 | FF | Z27 | Female toilet | Hanging Lights | FF_Z27_H01 |  | On click | 21.5 | 8 |  |  | 1 | 0.7 | 120.4 | 260 | 31304 | 2172 | 210.65
L1 | T09 | FF |  |  | Tube lights | FF_Z27_H02 |  | On click | 21.5 | 1 |  |  | 5 | 0.7 | 75.25 | 260 | 19565
L1 | T09 | FF |  |  | mirror light | FF_Z27_H03 |  | On click | 5 | 3 |  |  | 1 | 1 | 15 | 260 | 3900
L1 | T09 | FF |  |  | hand dryer | FF_Z27_H04 |  | Nameplate | 1500 | 1 |  |  | 1 | 1 | 1500 | 260 | 390000
L1 | T09 | FF |  |  | Exhaust fan | FF_Z27_H05 |  | On click | 20 | 12 |  |  | 4 | 0.7 | 672 | 260 | 174720
L1 | T09 | Second floor | [7 empty] | 1 |  |  |  | 1 |  | 260 | 0
L1 | T09 | SF | Z01 | Male toilet | Hanging Lights | SF_Z01_H01 |  | On click | 21.5 | 8 |  |  | 1 | 0.7 | 120.4 | 260 | 31304 | 2172 | 225.7
L1 | T09 | SF |  |  | Tube lights | SF_Z01_H02 |  | On click | 21.5 | 1 |  |  | 6 | 0.7 | 90.3 | 260 | 23478
L1 | T09 | SF |  |  | mirror light | SF_Z01_H03 |  | On click | 5 | 3 |  |  | 1 | 1 | 15 | 260 | 3900
L1 | T09 | SF |  |  | hand dryer | SF_Z01_H04 |  | Nameplate | 1500 | 1 |  |  | 1 | 1 | 1500 | 260 | 390000
L1 | T09 | SF |  |  | Exhaust fan | SF_Z01_H05 |  | On click | 20 | 12 |  |  | 4 | 0.7 | 672 | 260 | 174720
L1 | T09 | SF | Z02 | Open-plan office | Hanging Lights | SF_Z02_H01 |  | On click | 21.5 | 16 |  |  | 5 | 0.7 | 1204 | 260 | 313040 | 1180 | 1204
L1 | T09 | SF | Z02 |  | Laptop charging | SF_Z02_H02 |  | Clampmeter | 40 | 1 |  |  | 32 | 0.5 | 640 | 260 | 166400
L1 | T09 | SF | Z03 |  | Printer | SF_Z03_H01 |  | Clampmeter | 180 | 3 | 30 | 21 | 1 | 1 | 540 | 260 | 140400
L1 | T09 | SF | Z04 | Open-plan office | Hanging Lights | SF_Z04_H01 |  | On click | 21.5 | 16 |  |  | 6 | 0.7 | 1444.8 | 260 | 375648 | 1340 | 1444.8
L1 | T09 | SF | Z04 |  | Laptop charging | SF_Z04_H02 |  | Clampmeter | 40 | 1 |  |  | 40 | 0.5 | 800 | 260 | 208000
L1 | T09 | SF | Z05 |  | Printer | SF_Z05_H01 |  | Clampmeter | 180 | 3 | 30 | 21 | 1 | 1 | 540 | 260 | 140400
L1 | T09 | SF | Z06 | AHU | AHU rated power | SF_Z06_H01 |  | Nameplate | 1500 | 16 | 50 | 8 | 1 | 1 | 24400 | 260 | 6344000 | 0 | 45.15 | 24400
L1 | T09 | SF |  |  | Tube lights | SF_Z06_H02 |  | On click | 21.5 | 1 |  |  | 3 | 0.7 | 45.15 | 260 | 11739
L1 | T09 | SF | Z07 | Corridor | Hanging lights | SF_Z07_H01 |  | On click | 21.5 | 18 |  |  | 1 | 0.7 | 270.9 | 260 | 70434 |  | 270.9
L1 | T09 | SF | Z08 | Cabin | Hanging Lights | SF_Z08_H01 |  | On click | 21.5 | 12 |  |  | 1 | 0.8 | 206.4 | 260 | 53664 | 47 | 206.4
L1 | T09 | SF |  |  | Laptop charging | SF_Z08_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | SF |  |  | Phone charging | SF_Z08_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | SF | Z09 | Cabin | Hanging Lights | SF_Z09_H01 |  | On click | 21.5 | 12 |  |  | 1 | 0.8 | 206.4 | 260 | 53664 | 67 | 206.4
L1 | T09 | SF |  |  | Laptop charging | SF_Z09_H02 |  | Clampmeter | 60 | 1 |  |  | 1 | 1 | 60 | 260 | 15600
L1 | T09 | SF |  |  | Phone charging | SF_Z09_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | SF | Z10 | Cabin | Hanging Lights | SF_Z10_H01 |  | On click | 21.5 | 12 |  |  | 1 | 0.8 | 206.4 | 260 | 53664 | 47 | 206.4
L1 | T09 | SF |  |  | Laptop charging | SF_Z10_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | SF |  |  | Phone charging | SF_Z10_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | SF | Z11 | Elevator | Hanging lights | SF_Z11_H01 |  | On click | 21.5 | 0 |  |  | 1 | 1 | 0 | 260 | 0 |  | 0
L1 | T09 | SF | Z12 | Cabin | Hanging Lights | SF_Z12_H01 |  | On click | 21.5 | 12 |  |  | 1 | 0.8 | 206.4 | 260 | 53664 | 47 | 206.4
L1 | T09 | SF |  |  | Laptop charging | SF_Z12_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | SF |  |  | Phone charging | SF_Z12_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | SF | Z13 | Cabin | Hanging Lights | SF_Z13_H01 |  | On click | 21.5 | 12 |  |  | 1 | 0.8 | 206.4 | 260 | 53664 | 47 | 206.4
L1 | T09 | SF |  |  | Laptop charging | SF_Z13_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | SF |  |  | Phone charging | SF_Z13_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | SF | Z14 | Cabin | Hanging Lights | SF_Z14_H01 |  | On click | 21.5 | 12 |  |  | 1 | 0.8 | 206.4 | 260 | 53664 | 47 | 206.4
L1 | T09 | SF |  |  | Laptop charging | SF_Z14_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | SF |  |  | Phone charging | SF_Z14_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | SF | Z15 | Corridor | Hanging lights | SF_Z15_H01 |  | On click | 21.5 | 18 |  |  | 1 | 0.7 | 270.9 | 260 | 70434 |  | 270.9
L1 | T09 | SF | Z16 | Meeting room 3 | Light | SF_Z16_H01 |  | On click | 21.5 | 3 |  |  | 1 | 0.7 | 45.15 | 260 | 11739 | 568 | 45.15
L1 | T09 | SF |  |  | TV | SF_Z16_H02 |  | On click | 448 | 1 | 5 | 23 | 1 | 1 | 448 | 260 | 116480
L1 | T09 | SF |  |  | Laptop charging | SF_Z16_H03 |  | Clampmeter | 40 | 1 |  |  | 6 | 0.5 | 120 | 260 | 31200
L1 | T09 | SF | Z17 | Cabin | Hanging Lights | SF_Z17_H01 |  | On click | 21.5 | 12 |  |  | 1 | 0.8 | 206.4 | 260 | 53664 | 47 | 206.4
L1 | T09 | SF |  |  | Laptop charging | SF_Z17_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | SF |  |  | Phone charging | SF_Z17_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | SF | Z18 | Cabin | Hanging Lights | SF_Z18_H01 |  | On click | 21.5 | 12 |  |  | 1 | 0.8 | 206.4 | 260 | 53664 | 47 | 206.4
L1 | T09 | SF |  |  | Laptop charging | SF_Z18_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | SF |  |  | Phone charging | SF_Z18_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | SF | Z19 | Cabin | Hanging Lights | SF_Z19_H01 |  | On click | 21.5 | 12 |  |  | 1 | 0.8 | 206.4 | 260 | 53664 | 47 | 206.4
L1 | T09 | SF |  |  | Laptop charging | SF_Z19_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | SF |  |  | Phone charging | SF_Z19_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | SF | Z20 | Cabin | Hanging Lights | SF_Z20_H01 |  | On click | 21.5 | 12 |  |  | 1 | 0.8 | 206.4 | 260 | 53664 | 47 | 206.4
L1 | T09 | SF |  |  | Laptop charging | SF_Z20_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | SF |  |  | Phone charging | SF_Z20_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | SF | Z21 | Cabin | Hanging Lights | SF_Z21_H01 |  | On click | 21.5 | 12 |  |  | 1 | 0.8 | 206.4 | 260 | 53664 | 47 | 206.4
L1 | T09 | SF |  |  | Laptop charging | SF_Z21_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | SF |  |  | Phone charging | SF_Z21_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | SF | Z22 | Cabin | Hanging Lights | SF_Z22_H01 |  | On click | 21.5 | 12 |  |  | 1 | 0.8 | 206.4 | 260 | 53664 | 47 | 206.4
L1 | T09 | SF |  |  | Laptop charging | SF_Z22_H02 |  | Clampmeter | 40 | 1 |  |  | 1 | 1 | 40 | 260 | 10400
L1 | T09 | SF |  |  | Phone charging | SF_Z22_H03 |  | Clampmeter | 10 | 0.7 |  |  | 1 | 1 | 7 | 260 | 1820
L1 | T09 | SF | Z23 | Open-plan office | Hanging Lights | SF_Z23_H01 |  | On click | 21.5 | 16 |  |  | 6 | 0.7 | 1444.8 | 260 | 375648 | 1340 | 1444.8
L1 | T09 | SF | Z23 |  | Laptop charging | SF_Z23_H02 |  | Clampmeter | 40 | 1 |  |  | 40 | 0.5 | 800 | 260 | 208000
L1 | T09 | SF | Z24 |  | Printer | SF_Z24_H01 |  | Clampmeter | 180 | 3 | 30 | 21 | 1 | 1 | 540 | 260 | 140400
L1 | T09 | SF | Z25 | Open-plan office | Hanging Lights | SF_Z25_H01 |  | On click | 21.5 | 16 |  |  | 5 | 0.7 | 1204 | 260 | 313040 | 1180 | 1204
L1 | T09 | SF | Z25 |  | Laptop charging | SF_Z25_H02 |  | Clampmeter | 40 | 1 |  |  | 32 | 0.5 | 640 | 260 | 166400
L1 | T09 | SF | Z26 |  | Printer | SF_Z26_H01 |  | Clampmeter | 180 | 3 | 30 | 21 | 1 | 1 | 540 | 260 | 140400
L1 | T09 | SF | Z27 | Female toilet | Hanging Lights | SF_Z27_H01 |  | On click | 21.5 | 8 |  |  | 1 | 0.7 | 120.4 | 260 | 31304 | 2172 | 210.65
L1 | T09 | SF |  |  | Tube lights | SF_Z27_H02 |  | On click | 21.5 | 1 |  |  | 5 | 0.7 | 75.25 | 260 | 19565
L1 | T09 | SF |  |  | mirror light | SF_Z27_H03 |  | On click | 5 | 3 |  |  | 1 | 1 | 15 | 260 | 3900
L1 | T09 | SF |  |  | hand dryer | SF_Z27_H04 |  | Nameplate | 1500 | 1 |  |  | 1 | 1 | 1500 | 260 | 390000
L1 | T09 | SF |  |  | Exhaust fan | SF_Z27_H05 |  | On click | 20 | 12 |  |  | 4 | 0.7 | 672 | 260 | 174720
L1 | T09 | Terrace | [7 empty] | 1 |  |  |  | 1 | 0 | 260 | 0
L1 | T09 | TR | Z01 |  | Solar Panels | TR_Z01_H01 |  | On click |  | 1 |  |  | 120 | 1 | 0 | 260 | 0
L1 | T09 | TR | Z02 |  | Outdoor unit of split AC | TR_Z02_H01 |  | On click |  | 1 |  |  | 1 | 1 | 0 | 260 | 0
[18 empty] | Equipment | Lighting | HVAC
[8 empty] | Wh | [6 empty] | 297839.2 |  | 77438192 | 128926.4 | 42375.6 | 126537.2 | 297839.2
[8 empty] | kWh | [6 empty] | 297.8392 |  | 77438.192 | 128.9264 | 42.3756 | 126.5372 | 297.8392
[8 empty] | kWh per year | [9 empty] | 33520.864 | 11017.656 | 32899.672
46509.5173
[20 empty] | 79409.1893 | 123947.7093
[18 empty] | Equipment | Lighting | HVAC
[8 empty] | kWh / m2 | [8 empty] | Excel | 9.2959 | 3.0554 | 22.0215
[18 empty] | Office Building HVAC 3D GAME TRIAL 2 (01-01:31-12) ** Bangalore Karnataka IND ISHRAE WMO#=432950 2025-04-28 15:55:51 - EnergyPlus | Office Building HVAC 3D GAME TRIAL 2 (01-01:31-12) ** Bangalore Karnataka IND ISHRAE WMO#=432950 2025-04-28 15:55:51 - EnergyPlus | Office Building HVAC 3D GAME TRIAL 2 (01-01:31-12) ** Bangalore Karnataka IND ISHRAE WMO#=432950 2025-04-28 15:55:51 - EnergyPlus
[17 empty] | DB | 9.96 | 5.44 | 33.14
|  | Chiller pump (kWh) |  |  |  | 25.44
|  | Condensor pump |  |  |  | 23.88
[15 empty] | Building area | 3605.99
[15 empty] | Building energy excel | 123947.7093
[15 empty] | Building energy DB | 175989.66
[15 empty] | EPI excel | 34.3727
[15 empty] | EPI DB | 44

## AC
Cooling load estimate | Capacity: 50TR
Time | Load % |  |  |  | Load % | COP
9:00 | 30% | ASHRAE 90.1 |  |  | 85% | 6.3
10:00 | 45% |  |  |  | 80% | 6.25
11:00 | 65% |  |  |  | 75% | 6.2
12:00 | 80% |  |  |  | 65% | 6.1
13:00 | 85% |  |  |  | 60% | 6
14:00 | 80% |  |  |  | 50% | 5.8
15:00 | 75% |  |  |  | 45% | 5.7
16:00 | 60% |  |  |  | 35% | 5.4
17:00 | 50% |  |  |  | 30% | 5.2
18:00 | 35%
Time | Load % | Cooling Load (TR) | Cooling Load (kW) | COP | Energy Use (kWh) | Pump
9:00 | 30% | 15 | 52.7527 | 5.2 | 10.1448 | 0.31642
10:00 | 45% | 22.5 | 79.1291 | 5.7 | 13.8823 | 0.23123
11:00 | 65% | 32.5 | 114.2976 | 6.1 | 18.7373 | 0.17132 |  | 9.3687
12:00 | 80% | 40 | 140.674 | 6.25 | 22.5078 | 0.14262
13:00 | 85% | 42.5 | 149.4661 | 6.3 | 23.7248 | 0.1353
14:00 | 80% | 40 | 140.674 | 6.25 | 22.5078 | 0.14262
15:00 | 75% | 37.5 | 131.8819 | 6.2 | 21.2713 | 0.15091
16:00 | 60% | 30 | 105.5055 | 6 | 17.5843 | 0.18255
17:00 | 50% | 25 | 87.9213 | 5.8 | 15.1588 | 0.21176
18:00 | 35% | 17.5 | 61.5449 | 5.4 | 11.3972 | 0.28165
[5 empty] | 176.9164 | 1.9664
[6 empty] | 178.8828 | kW per day | 89.4414
10 |  | for | 260 | days |  | 46509.5173 | kW